## Fuel Truck Specs
Avgas 100LL Fuel Truck RFP
Attachment A - Specifications
Requested Minimum Specifications | Comply Yes/ No | Notes
Chassis
The vehicle chassis shall be a new Ford or RAM make, and the engine shall be gasoline powered, non-turbocharged
Chassis shall be appropriately specced for the application and wieght of the refueler
Engine Hour Meter
Chassis shall be equipped with at least one 12v power socket
Flashing Amber Beacon - mounted at the highest point of the vehicle
Backup alarm
Backup Camera
Air Conditioning
Master battery cut-off switch
Automatic Transmission
Tank
The tank shall be a 1000 gallon Aluminum tank built in accordance with NFPA 407 and DOT 406. Tank shall have baffles, overturn protection, non-slip walkway, water drain couplings and sumps, 20" manhole with self closing cover
Tank sump piping shall be capped at the end with cam-lock style dust cap
Tank shall be equipped with a spring rewind static grounding reel
Tank shall be equipped with an emergency shutoff system
All piping shall be aluminum with 150 PSI rated working pressure - soft line not acceptable
Tank shall be equipped with Scully system for secondary overfill prevention
Tank shall be equipped with a rear mounted aluminum laddder with OSHA approved handles at the top
Tank shall be equipped with a bottom load system and high level shutoff with pre-check. A gauge and shut-off valve shall be supplied immediately down stream of the bottom load adapter
Refueling System
Pump shall be Blackmer 2" positive displacement, self priming, PTO driven rated at 40GPM
Filtration shall be provided by filter/monitor with air relief & pressure relief as needed, and spring loaded drain valves. All filtration shall be latest edition.
Filter drain line shall be capped at the end with cam-lock style dust cap
Filter vessel can be either Parker Velcon or Facet but Parker Velcon filter elements are preferred.
Filter vessel/fueling system shall be equipped with a differential pressure limiting device that stops the flow of fuel if differential pressure exceeds 15psi. Manual reset.
Filter vessel shall be equipped with shut off valves on the inlet and outlet.
Provide TCS 3000 meter and register head, aviation grade, fully rated to 50 GPM with aluminum internals
Shall be equipped with a Hannay electric rewind single wrap hose reel with aluminum internals, shutoff valve, 1" x 50' aviation grade fueling hose with hose certification and an OPW 295 SA nozzle
PLC control to manage all systems
Brake interlock shall NOT be a Mico system
Compliance
Refueler must meet NFPA 407 and any other standards referenced by NFPA 407
Provide all placards to meet NFPA 407
Refueler must meet DOT 406 where applicable
Additional Included Features
Provide aluminum chock block holder with new aluminum wheel chocks
Provide weathertight aluminum storage box for spill kit
Canopy and structure to cover fueling equipment module
Fire extinguishers and holders shall be supplied with unit to meet NFPA 407 standards
Ladder rack to accommodate 4 or 6 foot step ladder
Provide standard package LED work lights in tank and pump area
Provide all necessary conduit pathways from cab to pump/meter area to wire a future printer and any wireless data transfer in case it is added at a later date
Warranty / Manuals
It shall come with a 5 year warranty on product tank and manufacturers warranty on chassis.
Provide digital operation and maintenance manuals and as-built schematics as well as a hard copy upon delivery